March 18, 2014

Mr. George Korvah, Manager

Environmental & Water Chemistry Branch

GSA Heating Operations & Transmission District

U.S. General Services Administration (GSA)

325 13th Street, SW

Washington, DC 20024

RE:	Permits to Construct and Operate Three (3) Emergency Diesel Generators at the U.S. General Services Administration Central Heating and Refrigeration Plant

Dear Mr. Korvah:

Pursuant to sections 200.1 and 200.2 of Title 20 of the District of Columbia Municipal Regulations (20 DCMR), a permit from the District Department of the Environment (the Department) shall be obtained before any person may construct and operate a stationary source in the District of Columbia. The application of the  U.S. General Services Administration (GSA) (the permittee) to construct and operate three (3) diesel fuel fired emergency generators at the permittee’s facility located at 325 13th Street SW, Washington, DC, per the submitted plans and specifications, has been reviewed:

| Equipment Location | Equipment Location Address | Generator (Engine) Size | Generator Serial Number | Permit No. |
| --- | --- | --- | --- | --- |
| U.S. GSA | 325 13th Street, SW Washington, DC 20024 | 1,250 kW (1,818 hp) | 2FN02408/ESO:BDZPF | 6796 |
| U.S. GSA | 325 13th Street, SW Washington, DC 20024 | 1,250 kW (1,818 hp) | 2FN02408/ESO:BDZPF | 6797 |
| U.S. GSA | 325 13th Street, SW Washington, DC 20024 | 1,250 kW (1,818 hp) | 2FN02408/ESO:BDZPF | 6798 |

Based on the submitted plans and specifications as detailed in the applications received July 25, 2013 with revised submittal received August 6, 2013, your application is hereby approved subject to the following conditions:

I.	General Requirements:

a.	The emergency generators shall be operated in accordance with the air pollution control requirements of 20 DCMR.

b.	These permits expire on March 17, 2019 [20 DCMR 200.4].  If continued operation after this date is desired, the owner or operator shall submit an application for renewal by December 17, 2018.

c.	Construction or operation of equipment under the authority of these permits shall be considered acceptance of its terms and conditions.

- The Permittee shall allow authorized officials of the District, upon presentation of identification, to:

1.	Enter upon the Permittee’s premises where a source or emission unit is located, an emissions related activity is conducted, or where records required by this permit are kept;

2.	Have access to and copy, at reasonable times, any records that must be kept under the terms and conditions of this permit;

3.	Inspect, at reasonable times, any facilities, equipment (including monitoring and air pollution control equipment), practices, or operations regulated or required under this permit; and

4.	Sample or monitor, at reasonable times, any substance or parameter for the purpose of assuring compliance with this permit or any applicable requirement.

- These permits shall be kept on the premises and produced upon request.

- Failure to comply with the provisions of these permits may be grounds for suspension or revocation. [20 DCMR 202.2]

g.	With 12 months of issuance these permits to operate this equipment, the Permittee shall submit a complete application or application amendment to obtain/modify a Title V operating permit pursuant to 20 DCMR Chapter 3 incorporating the conditions of these permits.

II.	Emission Limitations:

  - a.	Visible emissions shall not be emitted into the outdoor atmosphere from the generators, except that discharges not exceeding forty percent (40%) opacity (unaveraged) shall be permitted for two (2) minutes in any sixty (60) minute period and for an aggregate of twelve (12) minutes in any twenty-four hour (24 hr.) period during start-up, cleaning, adjustment of combustion controls, or malfunction of the equipment [20 DCMR 606.1]

b.	An emission into the atmosphere of odorous or other air pollutants from any source in any quantity and of any characteristic, and duration which is, or is likely to be injurious to the public health or welfare, or which interferes with the reasonable enjoyment of life or property is prohibited. [20 DCMR 903.1]

III.	Operational Limitations:

  - a.	The emergency generators shall not be operated in excess of 400 hours in any given 12 month period.  If operation beyond 400 hours is desired, the owner or operator shall submit an application to amend these permits to comply with the conditions of 20 DCMR 805 and 20 DCMR 204 as if the equipment were being installed new at that time and shall obtain the Department’s approval of such application prior to initiating such operation.

- With the exceptions specified in Condition III(c), the emergency generators shall be operated only during emergencies as follows:

1.   An electrical power outage due to: a failure of the electrical grid; on-site disaster; local equipment failure; or public service emergencies such as flood, fire, natural disaster, or severe weather conditions (e.g. hurricane, tornado, blizzard, etc.);

2.	For a period of up to 15 hours per calendar year when there is a substantial deviation of voltage or frequency from the electrical provider to the premises of 5 percent or more below standard voltage or frequency such that the equipment being supported cannot be safely or effectively operated; or

3.	When a sudden, unexpected event occurs that, if not immediately attended to, presents a safety or public health hazard, is necessary to protect equipment from damage, or is necessary to avoid imposing an unreasonable financial burden.  An emergency includes operations necessitated by non-routine failures of equipment, but it does not include voluntary demand reductions covered by Condition III (f).

- The emergency generators may be operated for the purpose of maintenance checks and readiness testing for a period not to exceed one hundred (100) hours per year. Any such operation shall be considered as part of the 400 hours allowed under Condition III (a) above. [20 DCMR 201]

- The emergency generators shall fire only diesel fuel which contains a maximum sulfur content of 15 ppm (0.0015 percent by weight) and either a minimum cetane index of 40 or a maximum aromatic content of 35 volume percent. [20 DCMR 201]

e.	The emergency generators shall be operated and maintained in accordance with the recommendations of the equipment manufacturer or to industry standards for similar models if manufacturer specifications are unavailable. [20 DCMR201]

f.	The emergency generators shall not be operated in conjunction with a voluntary demand-reduction program or any other interruptible power supply arrangement with a utility, other market participant, or system operator.

g.	At all times, including periods of startup, shutdown, and malfunction, the owner shall maintain and operate the emergency generators in a manner consistent with safety and good air pollution control practices for minimizing emissions Department which may include, but is not limited to, monitoring results, opacity observations, review of operation and maintenance procedures, review of operation and maintenance records, and inspection of the source. [20 DCMR 201]

IV.	Monitoring and Testing Requirements:

a.	The owner or operator shall monitor the date, time, duration, and reason for each emergency generator startup.

b.	In order to ensure compliance with Condition III (a), the owner or operator shall monitor the total hours of operation of each generator each month with the use of a properly functioning, non-resettable hour metering device or by tracking the sum of the duration of each instance of operation each month.

c.	The owner or operator shall test fuel oil as necessary to show compliance with Conditions III(d) and V(c) in accordance with appropriate ASTM methods. [20 DCMR 502.6]

d.	The owner or operator shall conduct and allow the Department access to conduct tests of air pollution emissions from any source as requested.  [20 DCMR 502.1]

V.	Record Keeping Requirements:

The following information shall be maintained at the facility for a period not less than five (5) years [20 DCMR 500.8 and 20 DCMR 302.1(c)(2)(B)]:

1.	The date, time, duration, and reason for each start-up of the emergency generators; (Note that if the unit is operated due to a deviation in voltage or frequency from the utility pursuant to Condition III(b)(2), this shall be specifically noted.)

2.	The total hours of operation for each month and the cumulative 12-month rolling period shall be calculated and recorded for each generator within 15 days of the end of each calendar month;

3.	The total hours of operation due to a deviation in voltage from the utility pursuant to Condition III (b)(2) each calendar year;

4.	Records of the maintenance performed on the unit;

5.	Records of the results of any visible emissions monitoring performed;

6.	Records of the occurrence and duration of each malfunction of operation; and

7.	Records of the actions taken during periods of malfunction to minimize emissions, including corrective actions to restore malfunction process and air pollution control and monitoring equipment to its normal or usual manner of operation.

b.	The owner or operator shall maintain a copy of each emergency generator’s manufacturer’s maintenance and operating recommendations at the facility.  If such documentation is unavailable, the owner or operator shall maintain documentation of the industry standards to which the unit is being maintained.

c.	For each delivery of diesel fuel, the owner or operator shall maintain one of the following:

1.	A fuel delivery receipt containing the date, fuel type, and amount of the delivery and certification from the fuel supplier that the fuel delivered was tested in accordance with an appropriate ASTM method (specified in the certification) and met the requirements of Condition III(d); or

2.	A fuel delivery receipt and documentation of sampling and analysis containing the following information:

A.	The fuel oil type;

B.	The concentration or weight percent of sulfur in the fuel;

C.	The date and time the sample was taken;

D.	The name, address, and telephone number of the laboratory that analyzed the sample; and

E.	The test method used to determine the sulfur content.

If you have any questions, please call me at (202) 535-1747 or Abraham T. Hagos at (202) 535-1354.

Sincerely,

Stephen S. Ours, P.E.

Chief, Permitting Branch

SSO:ATH