December 24, 2013					Permittee: Pepco Energy Services, Inc.

John Fratangelo, Vice President

Pepco Energy Services, Inc.

1300 N. 17th Street

Arlington, VA. 22209

RE:	Permits to Construct and Operate Two Natural Gas-fired Temporary Boilers

Dear Mr. Fratangelo:

Pursuant to sections 200.1 and 200.2 of Title 20 of the District of Columbia Municipal Regulations (20 DCMR), a permit from the District Department of the Environment (the Department) shall be obtained before any person can construct and operate a stationary source in the District of Columbia. The Permittee’s applications to operate the listed 250 hp Cleaver Brooks natural gas boilers located at the Blue Plains Wastewater Treatment Plant (WWTP) in Washington, DC, have been reviewed:

| Equipment Location | Address | Equipment Size (MMBTU/hr heat input) | Model Number | Permit No. |
| --- | --- | --- | --- | --- |
| Blue Plains WWTP | 5000 Overlook Ave. SW Washington DC | 9.9 | CB200-250S | 6809 |
| Blue Plains WWTP | 5000 Overlook Ave. SW Washington DC | 9.9 | CB200-250S | 6810 |

Based on the submitted plans and specifications as detailed in the applications received on October 21, 2013, the applications are hereby approved, and the construction and operation of the boilers are permitted, subject to the following conditions:

I.	General Requirements:

  - This approval is issued pursuant to the applicable air pollution control requirements of 20 DCMR for the construction and operation of the heating boilers.

b.	This set of permits will expire on December 23, 2014 [20 DCMR 200.4].  If continued operation after this date is desired, the owner or operator shall submit applications and justifications for extension by September 23, 2014.

c.	Construction or operation of equipment under the authority of this set of permits shall be considered acceptance of its terms and conditions.

- The Permittee shall allow authorized officials of the District, upon presentation of identification, to:

1.	Enter upon the Permittee’s premises where a source or emission unit is located, an emissions related activity is conducted, or where records required by this permit are kept;

2.	Have access to and copy, at reasonable times, any records that must be kept under the terms and conditions of this permit;

3.	Inspect, at reasonable times, any facilities, equipment (including monitoring and air pollution control equipment), practices, or operations regulated or required under this permit; and

4.	Sample or monitor, at reasonable times, any substance or parameter for the purpose of assuring compliance with this permit or any applicable requirement.

- This set of permits shall be kept on the premises and produced upon request.

- Failure to comply with the provisions of this permit document may be grounds for suspension or revocation. [20 DCMR 202.2]

g.	Emergency situations shall be handled in accordance with the provisions of 20 DCMR 302.7 (a) through (c).

h.	The Permittee shall notify the Department in writing within ten (10) days of the Auxiliary boiler achieving optimal operating range.

i.	Upon determination that the temporary boilers are no longer needed, the Permittee shall immediately cease operation, remove the temporary boilers from service and completely isolate the boilers from other services or production activities at the facility.

j.	 The Permittee must remove the wheel-mounted temporary boilers from the Blue Plains wastewater treatment plant grounds within thirty (30) days of complying with Condition I(i) above.

II.	Emission Limitations:

  - Each of the two (2) identical 9.9 million BTU per hour Cleaver Brooks natural gas –fired boilers, shall not emit pollutants in excess of those specified in the following table [20 DCMR 201]:

| Boiler Emission Limits |
| --- |
| Pollutant | Short-Term Limit (Natural Gas) (lb/hr) | Annual (ton/yr) |
| Carbon Monoxide (CO) | 0.36 | 1.56 |
| Oxides of Nitrogen (NOx) | 1.00 | 4.38 |
| Particulate Matter < 10 microns (PM10) | 0.10 | 0.43 |
| Volatile Organic Compounds (VOC) | 0.05 | 0.22 |
| Sulfur Dioxide (SO2) | 0.02 | 0.09 |

b.	Particulate matter emissions from each boiler shall not exceed 0.10 pound per million BTU. [20 DCMR 600.1]

c.	No visible emissions shall be emitted into the outdoor atmosphere from each boiler; except that no greater than 40% opacity (unaveraged) shall be permitted for two minutes per hour and for an aggregate of twelve minutes per 24-hour period during start-up, cleaning, soot blowing, adjustment of combustion controls, or malfunction.[20 DCMR 606.1]

d.	An emission into the atmosphere of odorous or other air pollutants from any source in any quantity and of any characteristic, and duration which is, or is likely to be injurious to the public health or welfare, or which interferes with the reasonable enjoyment of life or property is prohibited. [20 DCMR 903.1]

e.	Violation of standards set forth in Condition II(c), as a result of unavoidable malfunction, despite the conscientious employment of control practices, shall constitute an affirmative defense on which the Permittee shall bear the burden of proof.  Periods of malfunction shall cease to be unavoidable malfunctions if reasonable steps are not taken to eliminate the malfunction within a reasonable time. [20 DCMR 606.5]

f.	Where the presence of uncombined water is the only reason for failure of an emission to meet the requirements of Condition II(c), the latter shall not be applicable. [20 DCMR 606.7]

III.	 Operational Limitations:

a.	These boilers may be operated using only natural gas with a maximum sulfur content of 2.5 grains per 100 standard cubic feet.  No other fuel is permitted. [20 DCMR 201]

b.	The use of No. 2 fuel oil in the boilers at any time is prohibited and any violation of this condition renders this set of permits null and void. [20 DCMR 201]

c.	The boiler shall be operated at all times in a manner consistent with the manufacturer’s specifications for the equipment.

IV.	Monitoring and Testing:

a.	If a stack test to determine compliance with Condition II(a), (b), and/or (c) is requested by the Department in accordance with 20 DCMR 502.1, the written report of the results of such a stack test shall be furnished to the Department in accordance with the following requirements [20 DCMR 502]:

1.	One (1) original and one (1) copy of the test protocol shall be submitted to the following address a minimum of thirty (30) days in advance of the proposed test date.  The test shall be conducted in accordance with Federal and District requirements.

Chief, Compliance and Enforcement Branch

Air Quality Division

1200 First Street, NE

5th Floor

Washington, DC 20002

2.	The test protocol shall be approved by the District prior to initiating any testing.  Upon approval of the test protocol, the Company shall finalize the test date with the assigned inspector in the Permitting and Enforcement Branch.  The District must have the opportunity to observe the test for the results to be considered for acceptance.

3.	The final results of the testing shall be submitted to the District within sixty (60) days of the test completion.  One (1) original and one (1) copy of the test report shall be submitted to the address in Condition IV (a)(1) above.

4.	The final report of the results shall include the emissions test report (including raw data from the test) as well as a summary of the test results and a statement of compliance or non-compliance with permit conditions to be considered valid.  The summary of results and statement of compliance or non-compliance shall contain the following information:

A.	A statement that the owner or operator has reviewed the report from the emissions testing firm and agrees with the findings.

B.	Permit number(s) and condition(s) which are the basis for the compliance evaluation.

C.	Summary of results with respect to each permit condition.

D.	Statement of compliance or non-compliance with each permit condition.

5.	The results must demonstrate to the District’s satisfaction that the tested emission unit is operating in compliance with the applicable regulations and conditions of this permit; if the final report of the test results shows non-compliance the owner or operator shall propose corrective action(s).  Failure to demonstrate compliance through the test may result in enforcement action.

b.	At least once per month, during operation of each boiler, the Permittee shall conduct visual observations of the emissions from each boiler.  If no operations are occurring for a given boiler during a given month, this shall be so noted.  If emissions are visible, the Permittee shall make arrangements for prompt visible emissions testing by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A).  Such a test shall consist of a minimum of 30 minutes of opacity observations for the boiler in question and shall be performed while firing the same fuel as was in use when the visible emissions were observed.

c.	Regardless of whether or not emissions are observed pursuant to Condition IV (b) of this set of permits, the Permittee shall conduct a minimum of one visible emissions test of each boiler during the duration of this set of permits.  Such a test program shall consist of a minimum of 30 minutes of opacity observations of each boiler firing each fuel and shall be performed by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A).

d.	The Permittee shall conduct and allow the Department access to conduct tests of air pollution emissions from any source as requested. [20 DCMR 502.1]

V.	Record Keeping and Reporting Requirements:

The following information shall be maintained at the facility for a period not less than five (5) years [20 DCMR 500.8 and 20 DCMR 302.1(c)(2)(B)]:

a.	The Permittee shall keep records of the results of all emissions testing required for the boilers pursuant to Conditions IV (a), (b), (c), and (d).

b.	The Permittee shall maintain records of the amount of fuel used each month in each boiler.  These data shall be maintained in a rolling twelve month sum format [20 DCMR 500.2].

c.	Maintain onsite in a logbook (with each item initialed by the person verifying its accuracy) or a verifiable electronic system whose information can be certified as to its accuracy the following:

1.	Records of all routine and non-routine maintenance performed on the temporary boilers. The records shall include a description of the maintenance activity, any problem being corrected or other reason for the maintenance activity, and a statement indicating whether or not the problem was corrected;

2.	Records of any odor complaints received as well as any deviations from the requirements of Condition (II) of this set of permits, as well as any actions taken to correct any identified visible emissions;

3.	Records of any equipment shutdowns related to improper operation of a control device and records of any control device malfunction;

4.	Records of the training of the operators and maintenance staff to minimize the production of emissions during operation;

5.	Records of the results of any testing performed pursuant to Condition IV(d).

d.	Records of the date, time, and duration (in minutes) of any process monitor service outrages and the percent of the annual potential operating time that each process monitor is not operational (excluding quality assurance and routine scheduled maintenance activities ).  The percent downtime records shall be maintained on 12-month rolling basis; and

e.	The Permittee shall maintain and report a record of the quantities of natural gas consumed in the temporary boilers during construction or testing or operation.  This report shall be submitted within 30 days of completion of operation of the equipment or by the expiration date of this set of permits, whichever is earlier.

f.	Within 30 days of completion of operation of the equipment or by the expiration date of this set of permits, whichever is earlier, the Permittee shall submit a report of calculated emissions of the following pollutants from the temporary boilers for the duration of the shakedown period in which the boilers were operated:

1.	Oxides of Nitrogen (NOx),

2.	Carbon Monoxide (CO),

3.	Coarse Particulate Matter (PM10) including both filterable and condensable fractions,

4.	Fine Particulate Matter (PM2.5) including both filterable and condensable fractions,

5.	Oxides of Sulfur (SOx), and

6.	Volatile Organic Compounds (VOC).

This emissions report shall include information justifying how the emissions were calculated.  Emissions exceeding those listed in Condition II (a) shall be clearly identified in the report.

g.	All reports required pursuant to this set of permits shall be submitted to:

Chief, Compliance and Enforcement Branch

Air Quality Division

1200 First Street, NE

5th Floor

Washington, DC 20002

If you have any questions, please call me at (202) 535-1747 or John Nwoke at (202) 724-7778.

Sincerely,

Stephen S. Ours, P.E.

Chief, Permitting Branch

SSO:JCN