September 11, 2013

Mr. Thomas P. Jacobus, General Manager

Washington Aqueduct

U.S. Army Corps of Engineers, Baltimore District

5900 MacArthur Boulevard, N.W.

Washington, DC 20016-2514

Re: 	Permits to Operate Fuel-burning Equipment

Dear Mr. Jacobus:

Pursuant to sections 200.1 and 200.2 of Title 20 of the District of Columbia Municipal Regulations (20 DCMR), a permit shall be obtained from the District Department of the Environment (the Department) before any person may construct and operate a new stationary source in the District of Columbia.  The application of the Washington Aqueduct, U.S. Army Corps of Engineers, Baltimore District (the Permittee) to construct and operate the listed identical dual fuel-fired Scotch boilers described below and located in Washington, DC, has been reviewed:

| Equipment Location | Address | Equipment Size | Model Number | Serial Number | Permit Number |
| --- | --- | --- | --- | --- | --- |
| Dalecarlia WTP (Admin Building) | 5900 MacArthur Blvd. NW Washington DC | 5,240,000 Btu/hr | S4-X-125-15 | S625-15-27 | 6334-R1 |
| Dalecarlia WTP (Admin Building) | 5900 MacArthur Blvd. NW Washington DC | 5,240,000 Btu/hr | S4-X-125-15 | S625-15-28 | 6335-R1 |
| Dalecarlia WTP (Admin Building) | 5900 MacArthur Blvd. NW Washington DC | 5,240,000 Btu/hr | S4-X-125-15 | S625-15-26 | 6336-R1 |

Based on the submitted plans and specifications as detailed in your applications dated February 19, 2013 (letter of February 19, 2013), and received on February 26, 2013, your applications are hereby approved, and the operation of each of the emission source is permitted, subject to the following conditions:

- General Requirements:

  - This approval is issued pursuant to the applicable air pollution control requirements of 20 DCMR for the construction and operation of the heating boilers.

  - This set of permits expires on September 10, 2018 and if continued operation beyond this date is desired, the owner or operator shall submit an application for renewal by June 10, 2018. [20 DCMR 200.4]

c.	Operation of equipment under the authority of this permit document shall be considered acceptance of its terms and conditions.

- The Permittee shall allow authorized officials of the District, upon presentation of identification, to:

1.	Enter upon the Permittee’s premises where a source or emission unit is located, an emissions related activity is conducted, or where records required by this permit are kept;

2.	Have access to and copy, at reasonable times, any records that must be kept under the terms and conditions of this permit;

3.	Inspect, at reasonable times, any facilities, equipment (including monitoring and air pollution control equipment), practices, or operations regulated or required under this permit; and

4.	Sample or monitor, at reasonable times, any substance or parameter for the purpose of assuring compliance with this permit or any applicable requirement.

e.	This permit document shall be kept on the premises and produced upon request.

- Failure to comply with the provisions of this permit document may be grounds for suspension or revocation. [20 DCMR 202.2]

- Emergency situations shall be handled in accordance with the provisions of 20 DCMR 302.7 (a) through (c).

- Emissions Limitations:

  - Each of the boilers shall not emit pollutants in excess of those specified in the following table [20 DCMR 201]:

| Boiler Emission Limits |
| --- |
| Pollutant | Short-Term Limit (Natural Gas) (lb/hr) | Short-Term Limit (No. 2 Fuel oil) (lb/hr) |
| Carbon Monoxide (CO) | 0.432 | 0.187 |
| Oxides of Nitrogen (NOx) | 0.514 | 0.748 |
| Particulate Matter < 10 microns (PM10) | 0.010 | 0.075 |
| Volatile Organic Compounds (VOC) | 0.029 | 0.013 |
| Sulfur Dioxide (SO2) | 0.003 | 0.265 |

b.	No visible emissions shall be emitted into the outdoor atmosphere from the boilers; except that no greater than 40% opacity (unaveraged) shall be permitted for two minutes per hour and for an aggregate of twelve minutes per 24-hour period during start-up, cleaning, soot blowing, adjustment of combustion controls, or malfunction. [20 DCMR 606.1]

- Particulate matter emissions from each unit shall not be greater than 0.12 pounds per million BTU. (Permittee is deemed to have complied with this requirement by burning natural gas or No. 2 fuel oil unless other credible evidence of a violation of the standard is identified.) [20 DCMR 600.1]

- An emission into the atmosphere of odorous or other air pollutants from any source in any quantity and of any characteristic and duration which is, or likely to be injurious to the public health or welfare, or which interferes with the reasonable enjoyment of life and property is prohibited. [20 DCMR 903.1]

III.	 Operational Limitations:

  - These boilers may be operated using only natural gas with a maximum sulfur content of 2.5 grains per 100 standard cubic feet or No. 2 fuel oil/diesel fuel containing no greater than 0.0015 % sulfur by weight (15ppm). [20 DCMR 201].

  - This approval is valid for the specific activity cited in the application submitted to this office. Any deviation from the specific activity is a violation of this permit document.

  - The boilers shall be operated at all times in a manner consistent with the applicable manufacturer’s specifications for the boiler.

  - The Permittee shall perform tune-ups on each unit on a biennial basis.  The first tune-up must be performed by March 21, 2013.  Subsequent tune-ups must be conducted no more than 25 months after the previous tune-up. [40 CFR 63.11201(b) and 63.11223(a)]

  - In order to demonstrate continuous compliance, each tune-up shall be performed to meet the following criteria: [20 CFR 63.11223(b)]

1. 	As applicable, inspect the burner, and clean or replace any components of the burner as necessary (you may delay the burner inspection until the next scheduled unit shutdown, but you must inspect each burner at least once every 36 months).

2.	Inspect the flame pattern, as applicable, and adjust the burner as necessary to optimize the flame pattern. The adjustment should be consistent with the manufacturer's specifications, if available.

3.	Inspect the system controlling the air-to-fuel ratio, as applicable, and ensure that it is correctly calibrated and functioning properly.

4.	Optimize total emissions of carbon monoxide. This optimization should be consistent with the manufacturer's specifications, if available.

5.	Measure the concentrations in the effluent stream of carbon monoxide in parts per million, by volume, and oxygen in volume percent, before and after the adjustments are made (measurements may be either on a dry or wet basis, as long as it is the same basis before and after the adjustments are made).

6.	If the unit is not operating on the required date for a tune-up, the tune-up must be conducted within one week of startup

e.	At all times, including periods of startup, shutdown, and malfunction, the owner or operator shall, to the extent practicable, maintain and operate the unit in a manner consistent with good air pollution control practice for minimizing emissions.  Determination of whether acceptable operating procedures are being used will be based on information available to the Department which may include, but is not limited to, monitoring results, opacity observations, review of operating and maintenance procedures, and inspection of the source.

- Monitoring and Testing Requirements

a.	If a stack test to determine compliance with Condition II (a), (b) and/or (c) is requested by the Department in accordance with 20 DCMR 502.1, the written report of the results of such a stack test shall be furnished to the District in accordance with the following requirements [20 DCMR 502]:

1.	One (1) original and one (1) copy of the test protocol shall be submitted to the following address a minimum of thirty (30) days in advance of the proposed test date.  The test shall be conducted in accordance with Federal and District requirements.

Chief, Compliance and Enforcement Branch

Air Quality Division

1200 First Street NE

5th Floor

Washington, DC 20002

2.	The test protocol shall be approved by the District prior to initiating any testing.  Upon approval of the test protocol, the Company shall finalize the test date with the assigned inspector in the Permitting and Enforcement Branch.  The District must have the opportunity to observe the test for the results to be considered for acceptance.

3.	The final results of the testing shall be submitted to the District within sixty (60) days of the test completion.  One (1) original and one (1) copy of the test report shall be submitted to the address in Condition IV (a)(1) above.

4.	The final report of the results shall include the emissions test report (including raw data from the test) as well as a summary of the test results and a statement of compliance or non-compliance with permit conditions to be considered valid.  The summary of results and statement of compliance or non-compliance shall contain the following information:

A.	A statement that the owner or operator has reviewed the report from the emissions testing firm and agrees with the findings.

B.	Permit number(s) and condition(s) which are the basis for the compliance evaluation.

C.	Summary of results with respect to each permit condition.

D.	Statement of compliance or non-compliance with each permit condition.

5.	The results must demonstrate to the District’s satisfaction that the emission unit is operating in compliance with the applicable regulations and conditions of this permit; if the final report of the test results shows non-compliance the owner or operator shall propose corrective action(s).  Failure to demonstrate compliance through the test may result in enforcement action.

b.	The owner or operator shall test fuel oil as necessary to show compliance with Condition III (a) in accordance with appropriate ASTM methods. [20 DCMR 502.6]

c.	At least once per week, during operation of each boiler, the Permittee shall conduct visual observations of the emissions from each boiler.  If no operations are occurring for a given boiler during a given week, this shall be so noted.  If emissions are visible, the Permittee shall make arrangements for prompt visible emissions testing by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A).  Such a test shall consist of a minimum of 30 minutes of opacity observations for the boiler in question and shall be performed while firing the same fuel as was in use when the visible emissions were observed.

d.	Regardless of whether or not emissions are observed pursuant to Condition IV (c) of this permit, the Permittee shall conduct a minimum of one visible emissions test of each boiler each calendar year for each fuel burned since the last test required under this permit condition.  If the only combustion of a given fuel burned since the last test was burned during periodic testing required by this permit, no visible emission test for that fuel will be required under this condition.  Such a test program shall consist of a minimum of 30 minutes of opacity observations of each boiler firing each fuel and shall be performed by a person certified in accordance with EPA Reference Method 9 (40 CFR 60, Appendix A).

V.	Record Keeping and Reporting Requirements:

The following information shall be maintained at the facility for a period not less than five (5) years [20 DCMR 500.8 and 40 CFR 63.10(b)]:

a.	The Permittee shall keep records of the results of all emissions testing required for the boilers pursuant to Conditions IV (a), (c), and (d) of this permit.

b.	For each delivery of No. 2 fuel oil or diesel fuel, the owner or operator shall maintain one of the following:

1.	A fuel delivery receipt containing the date, fuel type, and amount of the delivery and   certification from the fuel supplier that the fuel delivered was tested in accordance with an appropriate ASTM method (specified in the certification) and met the requirements of Condition III (a); or

2.	A fuel delivery receipt and documentation of sampling and analysis containing the following information:

A.	The fuel oil type;

B.	The concentration or weight percent of sulfur in the fuel;

C.	The date and time the sample was taken;

D.	The name, address, and telephone number of the laboratory that analyzed the sample; and

E.	The test method used to determine the sulfur content.

d.	The Permittee shall maintain records of the number of hours each boiler is operated using the approved fuel each month.  These data shall be maintained in a rolling twelve month sum format. [20 DCMR 500.2]

e.	The Permittee shall maintain records of the amount of fuel used each month in the boilers.  These data shall be maintained in a rolling twelve month sum format. [20 DCMR 500.2]

f.	Maintain onsite and submit, if requested by the EPA Administrator or the Department, a biennial report containing the information in paragraphs V(f)(1) through (3) of this section.

1.	The concentrations of CO in the effluent stream in parts per million, by volume, and oxygen in volume percent, measured before and after the tune-up of the boiler.

2.	A description of any corrective actions taken as a part of the tune-up of the boiler.

3.	The type and amount of fuel used over the 12 months prior to the biennial tune-up of the boiler.

g.	If not already completed at the time of issuance of this permit, submit an “Initial Notification of Applicability”  to the EPA Administrator with respect to the applicability of 40 CFR 63, Subpart JJJJJJ, National Emission Standards for Hazardous Air Pollutants for Industrial, Commercial, and Institutional Boilers Area Sources as required by 40 CFR 63.11225(a)(4).

h.	Submit a biennial compliance report containing the following information with the annual Title V compliance certification required pursuant to the Title V Operating permit for the equipment covered by this permit upon issuance, or by March 1, 2013 (whichever occurs first) and every two years thereafter [40 CFR 63.11225(b)]:

1.	Company name and address;

2.	Statement by a responsible official, with the official's name, title, phone number, e-mail address, and signature, certifying the truth, accuracy and completeness of the notification and a statement of whether the source has complied with all the relevant standards and other requirements of this subpart.

3.	If the source experiences any deviations from the applicable requirements during the reporting period, include a description of deviations, the time periods during which the deviations occurred, and the corrective actions taken.

j.	The Permittee must keep a copy of each notification and report that was submitted to comply with 40 CFR 63, Subpart JJJJJJ and this section and all documentation supporting any Initial Notification or Notification of Compliance Status that was submitted. [40 CFR 63.11225(c)(1)]

k.	The Permittee must keep records to document compliance with the requirements of Condition III(d) and (e) as follows [40 CFR 63.11225(c)(2)]:

1.	Records must identify each boiler, the date of tune-up, the procedures followed for tune-up, and the manufacturer’s specifications to which the boiler was tuned.

2.	Records documenting the fuel type(s) used monthly by each boiler, including, but not limited to, a description of the fuel, including whether the fuel has received a non-waste determination by the Permittee or EPA, and the total fuel usage amount with units of measure.

l.	The Permittee must keep records of the occurrence and duration of each malfunction of each boiler, or of any associated air pollution control and monitoring equipment. [40 CFR 63.11225(c)(4)]

m.	The Permittee must keep records of all actions taken during periods of malfunction to minimize emissions in accordance with the general duty to minimize emissions in 40 CFR 63.11205(a), including corrective actions to restore the malfunctioning boiler, air pollution control, or monitoring equipment to its normal or usual manner of operation. [40 CFR 63.11225(c)(5)]

If you have any questions, please call me at (202) 535-1747 or John C. Nwoke at (202) 724-7778.

Sincerely,

Stephen S. Ours, P.E.

Chief, Permitting Branch

SSO:JCN